# SS145012/012 PHOTOELECTRIC SMODE DETECTOR IC

1. Product description

  - Basic function:

SS145012 is a CMOS LSI used for smoke detection. Ultra-low power analog and digital circuits are contained in it. Combined with an IR photoelectric chamber, this IC is used to detect smoke through receiving light scattered by tiny smoke particles going into the chamber. When smoke is detected, A burst of alarm sounds are generated by an external piezoelectric buzzer driven by the push-pull output of this IC.

1.2. Applications:

Smoke detection system.

2. Features:

Power supply range:			6V ～ 12V

Average supply current:		8uA

Operating temperature range:	-10 ～ 60℃

Ideal for battery powered applications.

3. Block diagram of this IC

4. Pin assignment

5.Pin description

| Pin No. | Symbol | Input/output | Functions |  |
| --- | --- | --- | --- | --- |
| 1,2 | C1,C2 |  | External capacitor connection | By connecting external capacitor, a voltage feedback amplifier is formed. The gain of it is determined by capacitor’s value. |
| 3 | DETECT | I | Detecting input | Connect a photodiode to supply a signal to the internal comparator. |
| 4 | STROBE | O | Strobe | A strobe voltage output, referenced to VDD. When output = VDD -5V, it enables other internal circuits. |
| 5,14 | ## VDD,GND |  | Power supply | To supply the power |
| 6 | IRED | O | Output signal | To output pulse drive signal for external NPN transistor which drives a IR photodiode. |
| 7 | I/O |  | Input/output | It can be used to connect up to 40 detectors to make auxiliary alarm, remote alarm, auto-dialer… |
| 8,9 | BRASS,SILVER | O | Push-pull driver’s output | Push-pull driver outputs signal to drive external buzzer to alarm, and to show various operation states. |
| 10 | FEEDBACK | I | Feedback terminal | To feed ‘silver’ signal back to the push-pull output driver circuit’s input |
| 11 | LED | O | Output signal | It is an open drain output, can drive LED directly. The LED can tell the detector’s various operation states. |
| 12 | OSC | I | Oscillator’s input | Connected to external R and C, which determine the internal oscillator’s frequency. |
| 13 | R1 |  | External R and C connecting terminal | Connected to external R and C, which determine the output pulse period of IRED. |
| 15 | LOW-SUPPLY | I | Low voltage detecting input | It connected to external resistor divider between VDD and LED to get a low supply alarm threshold voltage |
| 16 | TEST | I | Test terminal | This pin is normally low by an internal pull-down device. When it is set high, the IC enters into a simulated-smoke condition. When floating, this pin comes back to VSS (low) by pull-down device. |

6. Function of this IC:

6.1. The variable gain photoelectric amplifier is directly connected to IR detector (photodiode). The amplifier’s gain is determined by external capacitors C1 and C2. During standby, the amplifier’s gain is at minimum. Under smoke condition, the amplifier’s gain is at medium. Entering into test condition, the amplifier’s gain is at maximum. Additionally, under standby state, if the special supervisory circuit is activated to check the chamber’s sensitivity, the amplifier’s gain is also at its maximum.

6.2. Using VSS as its reference, the I/O pin can be used to connect up to 40 units together. When I/O pin is used as an input, its on-chip pull-down resistor can prevent noise from entering into the unit. Under smoke status, the unit activates I/O driver to send a signal to its interconnected units to activate remote alarm.

6.3. Display method: LED (connected to LED pin) flashing combined with alarm sound, indicates a LOCAL SMOKE condition. Only pulsating alarm sound without LED flashing indicates a REMOTE SMOKE condition.

7. Specifications:

7.1. Absolute maximum ratings(VSS as reference)

| Symbol | Parameter | Limits | Units |
| --- | --- | --- | --- |
| VDD | Supply voltage | -0.5 ～ +12 | V |
| VIN DC input voltage | C1, C2, Detect | -0.25 ～Vdd+0.25 |  |
|  | OSC, low-supply trip | -0.25 ～Vdd+0.25 |  |
|  | I/O | -0.25 ～Vdd+0.25 |  |
|  | Feedback | -15 ～+15 |  |
|  | Test | -1.0 ～Vdd+0.25 |  |
| IIN | DC input current | ±10 | mA |
| IOUT | DC output current | ±25 | mA |
| IDD | Supply current | +25/-150 | mA |
| PD | Power dissipation in still air, 5Sec | 1200 | mW |
|  | Continuous | 350 |  |
| TSTG | Storage temperature | -55 ～125 | ℃ |
| TL | Soldering temperature | 260 | ℃ |

7.2 DC Electrical characteristics(Ta=25℃,VSS as reference, unless otherwise indicated)

| Symbol | Parameters |  | Test condition | VDD | Min. | Max. | Unit |
| --- | --- | --- | --- | --- | --- | --- | --- |
| VDD | Power supply voltage range |  |  | -- | 6.0 | 12 | V |
| VTH | Supply threshold voltage, Low supply alarm voltage |  | Low supply trip voltage VIN = VDD/3 |  | 6.5 | 7.8 | V |
| IDD | Average supply current |  | Standby, (See sample figure) | 12 | -- | 8 | uA |
| iDD | Supply peak current |  | Strobe on, IRED off (See sample figure) | 12 | -- | 2.0 | mA |
| VIL | Low level input voltage, I/O Feedback Test |  |  | 9.0 9.0 9.0 |  | 1.5 2.7 7.0 | V |
| VIH | High level input voltage I/O Feedback Test |  |  | 9.0 9.0 9.0 | 3.2 6.3 8.5 |  | V |
| IIN | Input current OSC, Detect Low supply trip Feedback |  | VIN = VSS or VDD VIN = VSS or VDD VIN = VSS or VDD | 12 12 12 |  | ±100 ±100 ±100 | nA |
| IIL | Low level input current TEST |  | VIN = VSS | 12 |  | -1 | uA |
| IIH | Pull-down current Test I/O |  | VIN = VDD No local smoke, VIN = VDD No local smoke, VIN = 17V | 9.0 9.0 12 | 0.5 25 -- | 10 100 140 | uA |
| VOL | Low level output voltage, LED Silver, Brass |  | IOUT = 10mA IOUT = 16mA | 6.5 6.5 |  | 0.6 1.0 | V |
| VOH | High level output voltage Silver, Brass |  | IOUT = -16mA | 6.5 | 5.5 | - | V |
| VOUT | Output voltage (See pin description) | Strobe | Inactive, IOUT = -1uA Active, IOUT = 100uA to 500uA (load regulation) | - 9.0 | VDD-0.1 VDD-4.4 | - Vdd-5.6 | V |
|  |  | IRED | Inactive, IOUT =-1uA Active, IOUT =6uA (load regulation) | - 9.0 | - 2.25 | - 1 3.75 |  |
| IOH | High-level output current, I/O |  | Local smoke, VOUT =4.5V | 6.5 | -4 | -- | mA |
|  |  |  | Local smoke, VOUT = VSS (short-circuit current) | 12 | -- | -16 |  |
| IOZ | Output off-state leak current, LED |  | VOUT = VSS or VDD | 12 | - | ±1 | uA |
| VIC | Common-mode voltage range C1, C2, Detect |  | Local smoke, Pushbutton test or chamber sensitivity test | -- | VDD -4 | VDD -2 | V |
| VREF | Internal reference voltage of smoke comparator |  | Local smoke, pushbutton test or chamber sensitivity test | -- | VDD-3.08 | VDD-3.92 | V |

7.3 AC ELECTRICAL CHARACTERISTICS

(TA= 25℃,VDD = 9.0 V, Component Values: R1 = 100.0 K, C3 = 1500.0 pF, R2 = 7.5 MΩ)

| Symbol | Parameters | Test condition | Clocks | Min* | Typ** | Max* | Unit |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/fosc | Oscillator Period | Free-Running Sawtooth Measured at Pin 12 | 1 | 7.0 | 7.9 | 8.6 | ms |
| tLED | LED Pulse Period | No Local Smoke, and No Remote Smoke | 4096 | 28.8 | 32.4 | 35.2 | s |
|  |  | Remote Smoke, but No Local Smoke | - | Extinguished |  |  |  |
|  |  | Local Smoke or Pushbutton Test | 64 | 0.45 | 0.5 | 0.55 |  |
| tw(LED), tw(stb) | LED Pulse Width and Strobe Pulse Width |  | 1 | 7.0 | - | 8.6 | ms |
| tIRED | IRED Pulse Period | Smoke Test | 1024 | 7.2 | 8.1 | 8.8 | s |
|  |  | Chamber Sensitivity Test, without Local Smoke | 4096 | 28.8 | 32.4 | 35.2 |  |
|  |  | Pushbutton Test | 128 | 0.9 | 1.0 | 1.1 |  |
| tw(IRED) | IRED Pulse Width |  | Tf* | 94 |  | 116 | us |
| tr | IRED Rise Time |  | - | - |  | 30 | us |
| tf | IRED Fail Time |  | - | - |  | 200 | us |
| ton | Silver and Brass Temporal Modulation Pulse |  | 64 | 0.45 | 0.5 | 0.55 | s |
| toff |  |  |  | 0.45 | 0.5 | 0.55 |  |
| toffd |  |  | 192 | 1.35 | 1.52 | 1.65 |  |
| tCH | Silver and Brass Chirp Pulse Period | Low Supply or Degraded Chamber Sensitivity | 4096 | 28.8 | 32.4 | 35.2 | s |
| twCH | Silver and Brass Chirp Pulse Width |  | 1 | 7.0 | 7.9 | 8.6 | ms |
| tRR | Rising Edge on I/O to Smoke Alarm Response Time | Remote Smoke, No Local Smoke | - | - | 2! | - | ms |
| tstb | Strobe Out Pulse Period | Smoke Test | 1024 | 7.2 | 8.1 | 8.8 | s |
|  |  | Chamber Sensitivity Test, without Local Smoke | 4096 | 28.8 | 32.4 | 35.2 |  |
|  |  | Low Supply Test, Without Local Smoke | 4096 | 28.8 | 32.4 | 35.2 |  |
|  |  | Pushbutton Test | - | - | 1 | - |  |

*Oscillator period T (= Tr + Tf) is determined by the external components R1, R2, and C3 where Tr = (0.6931) R2 * C3 and Tf = (0.6931) R1 * C3.

The other timing characteristics are some multiple of the oscillator timing as shown in the table.

**Typicals are not guaranteed.

!Time is typical - depends on what point in cycle signal is applied.

8. Application sample figure

9. Calibration:

To enter calibration mode, pin16 (TEST) must be below VSS, pulling  more than 100uA continuously out of the pin for at least one OSC cycle. To exit this mode, the TEST pin is floated at least one OSC cycle.

Table. Configuration of pins in the calibration mode

| Description | PIN | Comments |
| --- | --- | --- |
| I/O | 7 | Forcing this pin = VDD, places photo amp’s output on pin2 when pin15= VDD, or on pin1 when pin15= VSS. |
| Low-supply | 15 | Low: normal gain of photo amplifier on pin1. High: supervisory gain on pin2. |
| Feedback | 10 | When pin15=low, driving it high enables gain with a hysteresis in the photo amp. |
| OSC | 12 | It equals to internal clock. |
| Silver | 9 | This pin becomes smoke comparator’s output. Positive pulses indicate that smoke has been detected. A static low level indicates no smoke. |
| Brass | 8 | This pin becomes the smoke integrator’s output. Static high level means two consecutive smoke detections. Static low level means two no-detections. |

SUNSTAR商斯达实业集团是集研发、生产、工程、销售、代理经销 、技术咨询、信息服务等为一体的高科技企业，是专业高科技电子产品生产厂家，是具有10多年历史的专业电子元器件供应商，是中国最早和最大的仓储式连锁规模经营大型综合电子零部件代理分销商之一,是一家专业代理和分銷世界各大品牌IC芯片和電子元器件的连锁经营綜合性国际公司。在香港、北京、深圳、上海、西安、成都等全国主要电子市场设有直属分公司和产品展示展销窗口门市部专卖店及代理分销商，已在全国范围内建成强大统一的供货和代理分销网络。 我们专业代理经销、开发生产电子元器件、集成电路、传感器、微波光电元器件、工控机/DOC/DOM电子盘、专用电路、单片机开发、MCU/DSP/ARM/FPGA软件硬件、二极管、三极管、模块等，是您可靠的一站式现货配套供应商、方案提供商、部件功能模块开发配套商。专业以现代信息产业（计算机、通讯及传感器）三大支柱之一的传感器为主营业务，专业经营各类传感器的代理、销售生产、网络信息、科技图书资料及配套产品设计、工程开发。我们的专业网站——中国传感器科技信息网（全球传感器数据库） www.SENSOR-IC.COM 服务于全球高科技生产商及贸易商，为企业科技产品开发提供技术交流平台。欢迎各厂商互通有无、交换信息、交换链接、发布寻求代理信息。欢迎国外高科技传感器、变送器、执行器、自动控制产品厂商介绍产品到 中国，共同开拓市场。本网站是关于各种传感器-变送器-仪器仪表及工业自动化大型专业网站,深入到工业控制、系统工程计 测计量、自动化、安防报警、消费电子等众多领域，把最新的传感器-变送器-仪器仪表买卖信息,最新技术供求,最新采购商,行业动态，发展方向，最新的技术应用和市场资讯及时的传递给广大科技开发、科学研究、产品设计人员。本网站已成功为石油、化工、电力、医药、生物、航空、航天、国防、能源、冶金、电子、工业、农业、交通、汽车、矿山、煤炭、纺织、信息、通信、IT、安防、环保、印刷、科研、气象、仪器仪表等领域从事科学研究、产品设计、开发、生产制造的科技人员、管理人员 、和采购人员提供满意服务。 我公司专业开发生产、代理、经销、销售各种传感器、变送器、敏感元器件、开关、执行器、仪器仪表、自动化控制系统： 专门从事设计、生产、销售各种传感器、变送器、各种测控仪表、热工仪表、现场控制器、计算机控制系统、数据采集系统、各类环境监控系统、专用控制系统应用软件以及嵌入式系统开发及应用等工作。如热敏电阻、压敏电阻、温度传感器、温度变送器、湿度传感器、 湿度变送器、气体传感器、 气体变送器、压力传感器、 压力变送、称重传感器、物（液）位传感器、物（液）位变送器、流量传感器、 流量变送器、电流（压）传感器、溶氧传感器、霍尔传感器 、图像传感器、超声波传感器、位移传感器、速度传感器、加速度传感器、扭距传感器、红外传感器、紫外传感器、 火焰传感器、激光传感器、振动传感器、轴角传感器、光电传感器、接近传感器、干簧管传感器、继电器传感器、微型电泵、磁敏（阻）传感器 、压力开关、接近开关、光电开关、色标传感器、光纤传感器、齿轮测速传感器、 时间继电器、计数器、计米器、温控仪、固态继电器、调压模块、电磁铁、电压表、电流表等特殊传感器 。 同时承接传感器应用电路、产品设计和自动化工程项目。

更多产品请看本公司产品专用销售网站:

商斯达中国传感器科技信息网：http://www.sensor-ic.com/

商斯达工控安防网：http://www.pc-ps.net/

商斯达电子 元器件网：http://www.sunstare.com/

商斯达微波光电产品网:HTTP://www.rfoe.net/

商斯达消费电子产品网://www.icasic.com/

商斯达军工产品网:http://www.junpinic.com/

商斯达实业科技产品网://www.sunstars.cn/传感器销售热线：

地址：深圳市福田区福华路福庆街鸿图大厦1602室

电话：0755-83607652 83376489 83376549 83370250   83370251   82500323

传真：0755-83376182  （0）13902971329  MSN: SUNS8888@hotmail.com

邮编：518033   E-mail:szss20@163.com     QQ: 195847376

深圳赛格展销部：深圳华强北路赛格电子市场2583号 电话：0755-83665529   13823648918 FAX:0755-82914956

技术支持: 0755-83394033 13501568376

欢迎索取免费详细资料、设计指南和光盘 ；产品凡多，未能尽录，欢迎来电查询。

北京分公司：北京海淀区知春路132号中发电子大厦3097号

TEL：010-81159046  82615020  13823791822  FAX：010-62543996

上海分公司：上海市北京东路668号上海賽格电子市场D125号

TEL：021-28311762  56703037  13823676822  FAX：021-56703037

西安分公司：西安高新开发区20所(中国电子科技集团导航技术研究所)

西安劳动南路88号电子商城二楼D23号

TEL：029-81022619  13072977981  FAX:029-88789382